## Slide 1: History, and Evolution of SCADA
© 2017 General Electric Company. All rights reserved.

## Slide 2: Origin and Purpose of SCADA

## Slide 3: Millions Of miles of distribution
One of the
Biggest Machine on Earth - America’s Power System
10,000
Power Plants
½ Million
Miles of Transmission
55,000
Substations

## Slide 4: Biggest Machine on Earth
Goal is to optimize the power production and delivery process
The collection, secure transfer, and analysis of end-to-end system information is required in order to achieve that goal

## Slide 5: SCADA: Supervisory Control and Data Acquisition
System state knowledge is crucial
Purpose of SCADA
Process optimization
System situational awareness
System control
Without it, essentially running blind

## Slide 6: Healthcare Analogy – Wellness Care
Monitor
Various real and long-term data Weight, heart rate, insulin level
Frequency
Periodically, relatively long interval As reasonable, appropriate and directed
Event based
Goal: Find and correct health issues Maintain and optimize health

## Slide 7: Power Production/Delivery System – Maintenance
Monitor
Various real and long-term data Temperature, power, gas concentration
Goal: Find and correct issues Maintain and optimize system health
Frequency
Periodically, relatively long interval As reasonable, appropriate and directed
Event based

## Slide 8: Healthcare Analogy – Emergency Room
Monitor
Critical real-time data
Heart rate, blood pressure, breathing rate
Frequency
Constant, short Interval
Actions: Immediate
Goal: Keep patient alive

## Slide 9: Power Production/Delivery System - SCADA
Actions: Immediate
Goal: Keep system alive and operational
Monitor
Critical real-time data Volts, amps, power, loads
Generation availability, breaker statuses
Frequency
Constant, short Interval

## Slide 10: Initial Implementations: Early to mid-1900s

## Slide 11: Power Plant Control Room
Power plant control rooms were first “control centers”
Extended to nearby substations for SCADA functionality
Directly-connected data sources
Device contacts
Electromechanical meters
State knowledge limited to immediate facilities
Moran Generating Station Courtesy of the Burlington Electric Department
Burlington, Vermont

## Slide 12: Power Plant Control Room
Power plant control rooms were first “control centers”
Essentially extended instrumentation
Dedicated discrete data indication and display board
Meters
Lamps

## Slide 13: Sources and Provision of Data
Extended instrumentation impractical for distant stations
Alternative manual methods
  Staffed stations
  On-call local area workers
  Public
Progressive application of telemetry
  Simple schemes
  Limited to crucial data

## Slide 14: Electronic-Based Systems: 1960s-1970s

## Slide 15: Supervisory Control and Data Collection
SCADA acronym came into use
Early implementation
  Field devices, predominantly at subs
  Remote data equipment (RDE)
    Standalone, independent
    Dedicated function
    Perform data acquisition
    Execute control actions

## Slide 16: Remote Data Equipment (RDE)
Hardware
Discrete electronics
Hardware-based logic
Often wire-wound connections
Multiple large low-density PCBs
Common card-cage format

## Slide 17: Local Input/Output (I/O)
Hard IO
Card-based
Local to RDE
Low-level analog inputs (AIs), typically
+/- 1mA transducer
Status inputs (DIs), typically equipment contacts
Control outputs (DOs)

## Slide 18: Energy Management System (EMS) Master
Computer / data processor
  Communications processor
  Communication with system devices
Protocol / language
Simple limited interface
Orpheum Electric building Courtesy of Iowa Electric
Sioux City, Iowa

## Slide 19: Master-to-RDE Communications
Objectives
  Move data
  Optimize bandwidth usage
  Minimize impact on processor and memory
RDE and master sourced from common vendor using proprietary vendor-specific protocol, e.g., Conitel, CDC, Telegyr
Near-zero concern for interoperability
Protocol / language
  Poll-response scheme
  Bit and byte orientations
  Often hardware-associated
SCADA Master Station/Control Center
Comm. Links
Remote Substation
Local I/O
HMI/SCADA
Master
Protocol
Radio Microwave Spread-spectrum
Various Media
Remote Terminal Unit (RTU)
Controls
Statuses
Analogs

## Slide 20
Protocol Hardware Association
Message segments match hardware I/O cards e.g., Leeds & Northrup Conitel protocol

## Slide 21: Communications Media
4-wire leased party phone lines
Microwave
Radios
Typically FSK via 1200 baud modem

## Slide 22: Microprocessor-Based Systems: 1980s-1990s

## Slide 23: Remote Terminal Unit (RTU)
Microprocessor-based
Firmware based logic and processing
Implemented advanced functionality
  PLC
  Multiple master support
  Calculator, etc.
Communications to master
  Leased phone lines
  Microwave
  Radio, licensed and spread spectrum
  Fiber, mostly multiplexed serial channels

## Slide 24: I/O and Local Communication
IO
Predominantly local hard IO
Distributed IO for large stations
Utilize data in IEDs
  Meters
  Relays
  Controls (e.g., LTC, regulator, etc.)
Communications media to IEDs:
  RS232 serial
  RS485 serial
  Some fiber serial
  Some Ethernet, copper and fiber

## Slide 25: Communication Protocols
Vendors started to emulate other vendors’ protocols
  Meters
  Relays
  Controls (e.g., LTC, regulator, etc.)
Westronic created DNP protocol
  Interoperable
  Critical need for RTU-to-IED comms
  Publicly released to DNP Users Group
  Industry game changer

## Slide 26: Energy Management System Master
Increased processor and memory
More remote stations monitored
Advanced graphical user interface (GUI) display board
  CRT
  Projection

## Slide 27: Current Systems of the 2000s-2010s and the Migration to Multifunction Gateways

## Slide 28: Energy Management System Master
Many continued to utilize vendor-specific protocols
Implemented advanced functionality
  Load control
  State estimators

## Slide 29: Energy Management System Master
Advanced Graphical User Interface (GUI)

## Slide 30: Remote Terminal Unit (RTU) / Gateway
Moved toward substation Gateway design/concept
Hard IO agnostic - Use IED data or 3rd party IO modules
Data primarily sourced from IEDs
  Operational real time data
  Classic status and analog values
  Non-operational data
    Events
    Logs

## Slide 31: Gateway Multifunctionally
Advanced Automation Automate substation procedures using IEC 61131 compliant tools
Fault Recording & Data Logging and File Retrieval
Extract valuable data such as digital fault records and event files
Secure Remote Access
Securely access substation device locally and remotely
Redundancy
Hot & Warm-standby, PRP and HSR
Advanced Gateway
Data collection from substation IEDs for control & secure monitoring
Embedded HMI
Customizable local or remote HMI with multiple windows

## Slide 32: Gateway Multifunctionally

## Slide 33: Communications Media
Drastic reduction in bandwidth constraints
  Serial: 1200 baud to 56 kbaud channels
  LAN: 1MB to 1GB
  Frame relay, SONET, MPLS, etc.
Drastic reduction of communication costs
  Standards such as Ethernet and TCP/IP
  Explosion of communications market
  Advances in hardware capabilities

## Slide 34: Communications Protocols
Evolution of interoperable protocols
DNP additions
UCA evolution to, and development of IEC 61850
  Specifies how data shall be moved
  Manufacturing Message Specification (MMS)
    Client/server scheme
  Generic Object-Oriented Substation Event (GOOSE)
    Publisher/subscriber scheme

## Slide 35: Future Implementations and Direction of SCADA

## Slide 36: Impacts of Technology
Wide variety of communications technologies available
Bandwidth costs no longer the driver they used to be
Greater system and device intelligence and need for situational awareness requires:
  More points to be monitored and reported
  More data to be obtained and processed
  Increased complexity in applications
  Focus is shifting from data acquisition to data management

## Slide 37: Focus Shift
Data acquisition to data management
Manage huge amounts of data and datasets
Configuration of devices and applications
Maintenance of devices and applications
Updating devices
Securing devices and configurations
These will be the main cost drivers

## Slide 38: Impacts of Technology
Application of data analysis tools
Processing boatloads of data into information
Mining data for useful information
Efficient reporting of data to those who need it

## Slide 39: Data Management
Higher commissioning costs
More applications accessing data
Deregulation adds complexity due to increased sharing

## Slide 40: Traditional SCADA Data Management
Meanings of points maintained in multiple places
Configuration of RTU and IEDs
  Configuration of databases
  Configuration of applications
  Protocols were primarily register based

## Slide 41: Traditional SCADA Data Management
Validation is costly and time consuming
Example: Move point 3851 from its source to multiple destinations
  The point is referenced by its stack location
  A meaning must be assigned to the point
  The meaning must be consistent and tracked throughout the system
  The point must be manually managed and validated
  The effort is complex and expensive

## Slide 42: Communication and Data Management Trends
Industries moving toward object-oriented protocols
Data organized by function
Simplifies distributed applications and their management
Standardized objects for interoperability
Self-description and meta-data allow for online validation
  Objects aren’t just bytes of data but also descriptions
Bandwidth is the tradeoff
  Connecting applications to data is bigger effort/obstacle than the bandwidth to move it

## Slide 43: Modern Object-Oriented Protocols
Goal: Reduce data management while maintaining high integrity and reliability
IEC 61850 standard objectives
  Address data management costs via modern communication techniques
  High degree of interoperability via standard objects
  Simplify config effort via common config language
  On-line validation of comm via metadata and self-description
Source: “UCA & 61850 for Dummies.” – Douglas Proudfoot

## Slide 44: Modern Object-Oriented Protocols
IEC 61850
Much broader than traditional protocols
Multiple protocols
  GOOSE, MMS, Sampled values
Standardized configuration language
  Substation Configuration Language (SCL)
  Extensible Markup Language (XML)
Standard and extensible objects
  Naming
  Data types

## Slide 45: SCL CID Example File

## Slide 46: Advanced Functionality
Gateway Evolution
  Advanced functionality
  Time synchronization and distribution: IRIG-B, SNTP, PRP
  Programmable logic
  Non-operational file gathering and reporting
Advanced processing platform
  Virtual machines
  Multiple OS environment
  Container-based technology
Container Engine (Digitally Signed)
Host Operating System
Optional Windows
Application 1
Application 2
Application 3
Application 4
Application 5
Downloadable Apps
Windows App 1
Windows App 2

## Slide 47: Gateway Security
Authentication, authorization, and audit trails
Secure perimeter access point and gateway
Remote tunneling (pass-through) connection to IEDs
Secure protocols
Secure firmware, configs, hardware
Automated retrieval and reporting
Password management
Firmware management

## Slide 48: Summary
Substation RTU
– Moving toward a multifunction gateway platform with
advanced functionality
Substation Data
  Volume will increase, primarily non-operational data
  Efficient, reliable, and secure management of data will be main objectives
  Application of analytical tools to convert data to useful information

## Slide 49: Summary
Communications
  Industry is moving toward object-oriented communications and protocols
  Interoperability, validation, self-identification will be key objectives
Cybersecurity
  Critical infrastructure protection will be crucial focus
  Automated management of firmware and passwords is key
  Compliance with mandates from governing bodies

## Slide 50: Questions?
© 2017 General Electric Company. All rights reserved.
© 2020 General Electric Company. All rights reserved.